## Slide 1: Stochastic Approaches for Reserve Determination and Operational Planning
Erik Ela, Eamonn Lannoye, Bob Entriken, Aidan Tuohy eela@epri.com
IEEE Power and Energy Society General Meeting
July 19, 2016

## Slide 2: Agenda
Operating reserves and advanced scheduling
  What do they do
  Why are they needed
  How can they be used differently
Comparison of Advanced Scheduling
and dynamic operating reserve
reserve requirements
  Intra-interval variability vs. high temporal
  resolution scheduling model
  Uncertainty vs. stochastic unit commitment

## Slide 3: Definitions (for this presentation)
Operating Reserve: Active Power Capacity that is held above or below expected average energy levels to respond to changing system conditions
Dynamic Reserve Requirements: Reserve requirements that may change based on actual and/or anticipated system conditions
Stochastic Programming/unit commitment: Scheduling application that enables schedules to meet multiple potential system conditions at least expected costs
Probabilistic forecasts: Scenario-forecasts with associated probabilities
Look-ahead modeling: Scheduling applications that optimize over multiple periods in the future
Variability: Changes in system conditions across time (may be expected)
Uncertainty: Changes in system conditions across decision horizons (not expected)
Explicit reserve: Met through reserve requirement constraint
Implicit reserve: Met through a scheduling procedure which inherently schedules reserve
Multi-cycle Modeling: Suite of scheduling tools with cycling decision points with decisions that mimic actual steady-state operations

## Slide 4: Impact of Holding Reserve
DASCUC
IDSCUC
RTSCUC
RTSCED
AGC
Day-ahead
Few-hours ahead
30-minutes ahead
10-minutes ahead
Seconds ahead
Steam Turbine Commitments
Dispatch output
Combustion Turbine Commitments
Combined Cycle Commitments
Regulation control
Reduce Costs
Reduce Price Spikes
Reduce ACE
Primary Impact of Holding Reserve

## Slide 5: Operating Reserve Need
Hold capacity now to meet the variability that occurs within the current scheduled time interval.
Hold capacity now to prepare for anticipated variability that occurs after the current time interval.
Hold capacity now to prepare for uncertain outcomes that occur in current or future scheduled time intervals.

## Slide 6: Three Central Reserve Needs
Chart: Power (MW)
Forecast
Interval Average
Actual
Inter-Interval Variability
Average Interval Uncertainty
Intra-Interval Variability
Risk Tolerance
Operating Reserve Need

## Slide 7: Meeting Operating Reserve Needs Implicitly Through Advanced Scheduling Applications
Three Central Needs for Reserve | Explicit Reserve Requirement | Implicitly Scheduled Flexibility
1. Variability occurring within the interval | Reserve Requirements (e.g., regulation reserve) | Shorter scheduling intervals
2. Variability anticipated beyond the interval | Reserve Requirements (e.g., flexible ramping reserve) | Time-coupled multi-period dispatch w/ longer look-ahead horizons
3. Uncertainty of future conditions | Reserve Requirements (e.g., contingency reserve) | Stochastic or robust unit commitment and dispatch meeting multiple scenarios

## Slide 8: Case Study Approach – Three Studies, Three Cases
Study the impact of dynamic reserve and advanced scheduling for each of the three reserve needs
  Study 1: Variability within the scheduling interval (Intra-Interval Variability)
  Study 2: Variability beyond the scheduling interval (Inter-Interval Variability)
  Study 3: Uncertainty throughout (Uncertainty)
Determine dynamic reserve requirements by using detailed, but attainable data to meet each of the three needs
Case 1: Simulate base case without dynamic reserve or advanced scheduling
Case 2: Simulate the advanced scheduling case
Case 3: Simulate the dynamic reserve case
Compare the cases in terms of reliability (inability to meet load, penalties) and efficiency (overall production costs)
These three studies are first performed on IEEE RTS

## Slide 9: Scheduling Cycle Definitions
PSO: Power Systems Optimizer

## Slide 10: Explicit vs. implicit – Intra-Interval variability
 | stdev | Max | Min | MAE | 95th %ile
Hourly | 46.7 | 207.2 | -102.4 | 33.9 | 77.2
15 m | 30.0 | 157.6 | -93.6 | 20.0 | 49.7
Error between Schedule and Actual

## Slide 11: Dynamic Reserve Requirements – Intra-Interval variability
Load of dynamic reserve case only is reduced when LFU1 makes total capacity excessively high. Remember the UC only cares about commitment and not dispatch!
H: Hour index
IH: 15-minute interval index within H

## Slide 12: Time/Cycle Model – Intra-interval Variability Study
Cycle | Decision Time | Binding Time | Horizon Length | Binding Periods in same decision cycle |  | Non-Binding Periods in same decision cycle | 
 |  |  |  | Number of Periods | Period Length | Number of Periods | Period Length
DAUC | 15 hours 5 minutes | 24 hours | 48 hours | 24 | 1 hour | 12 | 2 hour
HAUC | 4 hours 5 minutes | 1 hour | 5 hours | 1 | 1 hour | 4 | 1 hour
RTUC | 35 minutes | 15 minutes | 3 hours | 1 | 15 minutes | 11 | 15 minutes
RTED | 5 minutes | 15 minutes | 1 hour | 3 | 5 minutes | 9 | 5 minutes
Cycle | Decision Time | Binding Time | Horizon Length | Binding Periods in same decision cycle |  | Non-Binding Periods in same decision cycle | 
 |  |  |  | Number of Periods | Period Length | Number of Periods | Period Length
DAUC | 15 hours 5 minutes | 24 hours | 48 hours | 24 | 1 hour | 12 | 2 hour
HAUC | 4 hours 5 minutes | 1 hour | 5 hours | 4 | 15 minutes | 16 | 15 minutes
RTUC | 35 minutes | 15 minutes | 3 hours | 1 | 15 minutes | 11 | 15 minutes
RTED | 5 minutes | 15 minutes | 1 hour | 3 | 5 minutes | 9 | 5 minutes
Base Case and Dynamic Reserve Case
Advanced Scheduling Case

## Slide 13: Results – Intra-Interval Variability

## Slide 14: Dynamic Reserve Requirements – Uncertainty
Load of dynamic reserve case only is reduced when LFU1 makes total capacity excessively high. Remember the UC only cares about commitment and not dispatch!
S: Scenario index; T: Time index
IT,S: 15-minute interval at T for scenario S
M: Median scenario (used as scenario for deterministic case (could also be avg.)

## Slide 15: Uncertainty Driven Reserve Requirements
System Peak Load: 2100 MW Avg. Wind: 450 MW
Uncertainty modeled through bootstrapping method

## Slide 16: Time/Cycle Model – Uncertainty Case
Cycle | Decision Time | Binding Time | Horizon Length | Binding Periods in same decision cycle |  | Non-Binding Periods in same decision cycle | 
 |  |  |  | Number of Periods | Period Length | Number of Periods | Period Length
DAUC | 15 hours, 5 minutes | 24 hours | 48 hours | 24 | 1 hour | 12 | 2 hour
HAUC | 90 minutes | 1 hour | 5 hours | 4 | 15 minutes | 8 | 30 minutes
RTUC | 35 minutes | 15 minutes | 1 hour | 1 | 15 minutes | 3 | 15 minutes
RTED | 5 minutes | 15 minutes | 15 minutes | 3 | 5 minutes |  | 
Used in all cases
In the advanced scheduling case, the HAUC uses stochastic UC with 3 scenarios, a median scenario at 0.7 probability, a low at 0.15, and a high at 0.15. Only VG is stochastic.

## Slide 17: Results - Uncertainty

## Slide 18: CAISO Case Study
Perform the exact version of the “Uncertainty Study” on the Western Interconnection, with focus on CAISO system
Perform several sensitivities to understand additional sensitivity
Simulating the WI/CAISO system provides new challenges and new understandings
  Impact of interchange across regions
  Impact of existing static reserve requirements (e.g., spin and regulation) on dynamic load following / flexibility reserve
  Impact of more diverse resource mix (e.g., energy limited resources, demand response, etc.)
  Impact of transmission constraints
  Scalability of stochastic model on large, practical-sized systems

## Slide 19: CAISO STUDY RESULTS: COSTS & RELIABILITY
Stochastic scheduling increases costs by < 0.25% but reduces contingency reserve depletion by 80%.
Changing the number of scenarios and scenario weighting impacts the outcome marginally. Further work to determine translation into equivalent reserve needed.

## Slide 20: Case Study Results and Takeaways
In all three studies, advanced scheduling tends to perform the best
  Sometimes not by large margin and not in both categories
Hard to compare reliability and costs simultaneously
  Assuming a “loss of load” cost has its own challenges
Stochastic case takes at least 5X longer than dynamic reserve case to solve
  5-day CAISO/WI simulation with real-time unit commitment cycle using 10 scenarios takes 30 hours to solve using SOA software
  Deterministic cases takes 5 hours to solve
Further improvement can be made to the dynamic reserve requirement
  Locational requirements
  Deployment costs