## Slide 1: Practical Experience from the Blue Cut Fire Disturbance
Ryan D. Quint, PhD, PE
North American Electric Reliability Corporation

## Slide 2: NERC Disturbance Reports and Alerts

## Slide 3: Blue Cut Fire Disturbance

## Slide 4: Bulk System Phase Jump – During Fault

## Slide 5: Inverter PLL and Frequency Calculation
This is key!

## Slide 6: Modeling Frequency-Related Relays in Simulations
Source: [WECC, PEACE®]
Source: [PowerWorld]

## Slide 7: Key Takeaways
Blue Cut Fire Disturbance
  Erroneous tripping on calculated frequency
  Specific to one solar PV inverter manufacturer
  Problem addressed across entire fleet of BPS-connected inverters
  Have not seen this issue since
Simulations
  Careful using frequency-related relay models in studies
  Assure that those models are using some form of voltage inhibit function and/or are filtering the frequency signal before taking action
  Use “monitor only” mode, as a precaution