## Slide 1: Robust Bus Frequency Estimation for Power System Monitoring and Control
IEEE PES GM 2019 Panel
Local Frequency Measurements for System Control
Assistant Professor
Department of Electrical and Computer Engineering
Mississippi State University
Starkville, MS, 39762, USA
Junbo Zhao, Ph.D.
Acknowledgement-Professor Lamine Mili and Federico Milano

## Slide 2: Outline
Motivations and Challenges
Proposed Robust Bus Frequency Estimator
Frequency divider formulation
Measurement-driven frequency divider
Application for COI frequency monitoring
Results and Discussions
Conclusions

## Slide 3: Frequency Monitoring- Motivations
Source: Solar in US-NREL
Integration of high penetration of DERs reduces the relative inertia of the bulk power systems, leading to increased concern of frequency stability.
Source: EV in US-IHS Automotive

## Slide 4: 2016 South Australian Blackout
Source: 2016 South Australian blackout
(ROCOF) was too high for activating under frequency
load shedding under high penetration of DERs;

## Slide 5: Frequency Monitoring- Motivations
Synchrophasor measurements at 30-60 samples/s, provide the opportunity to capture power system frequency dynamics.
Source: www.naspi.org

## Slide 6: Frequency Monitoring- Challenges
Integration of DERs and flexible loads adds additional uncertainties to the system;
[R1] J. Nutaro and V. Protopopescu, “Calculating frequency at loads in simulations of electro-mechanical transients,” IEEE Trans. Smart Grid, vol. 3, no. 1, pp. 233–240, Mar. 2012.
[R2] F. Milano and A. Ortega, “Frequency divider,” IEEE Trans. Power Syst., vol. 32, no. 2, pp. 1493–1501, Mar. 2017.
There is a limited number of PMUs and the monitoring of the frequency of every bus is challenging;
The derivative of voltage angle with respect to time may yield sudden change of calculated bus frequency, triggering unnecessary frequency protection relays;
Dynamic simulation-based frequency divider formulation is time-consuming for large-scale systems.

## Slide 7: Frequency Monitoring- Challenges
Simulation of a 3‐phase fault to ground near a generator
[R3] WECC White Paper on Understanding Frequency Calculation in Positive Sequence Stability Programs

## Slide 8: Frequency Monitoring- Challenges
[R4] NREC-1200 MW Fault Induced Solar Photovoltaic Resource Interruption Disturbance Report.
2016 Southern California solar event: inaccurate local inverter frequency measurement provided by the PLL, triggering erroneous relay actions.
Notes: By the end of the day, the SCE transmission system experienced thirteen 500 kV line faults and the LADWP system experienced two 287 kV faults as a result of the fire. Four of these fault events resulted in the loss of a significant amount of solar PV generation.

## Slide 9: Problem Formulation
Objective: Given a limited number of PMUs, estimate the frequency at every bus of a system via the frequency divider.
where and are generator current injections and internal emfs; and are bus current and voltage injections; is the network admittance matrix; , and are admittance matrices.
Frequency divider formulation
The relationship between current and voltage phasors
can be expressed as follows:

## Slide 10: Frequency Divider
Since load current injections are negligible compared with that of the synchronous generators, we get
It can be further rewritten as:
Taking time derivatives on both sides of the above equation in rotating reference frame, i.e., dq frame, we get
where is the nominal rotor speed.

## Slide 11: Frequency Divider
Define , the analytical relationship between bus frequency and generator rotor speeds can be derived as
Remark: the bus frequency is correlated with each synchronous generator in the system, but the degree of participation of each generator on bus frequency is determined by the transmission and generator parameters.
[R2] F. Milano and A. Ortega, “Frequency divider,” IEEE Trans. Power Syst., vol. 32, no. 2, pp. 1493–1501, Mar. 2017.

## Slide 12: Frequency Divider-Challenges
contains transmission system and generator parameters, which has inherent uncertainties;
Dynamic simulation is required to obtain generator rotor speeds, which is challenging for large-scale system with various devices of different complexities;
The number of PMUs is limited and PMU only measures the bus frequency instead of generator internal rotor speed;
PMU measurements may contain gross errors due to GPS issues, impulsive noise, etc.

## Slide 13: Robust Bus Frequency Estimator
[R5] J. B. Zhao, L. Mili, F. Milano, "Robust frequency divider for power system online monitoring and controls," IEEE Trans. Power Systems, vol. 33, no. 4, pp. 4414-4423, 2018.
Proposed decentralized-centralized bus frequency estimation framework

## Slide 14: Robust Bus Frequency Estimator
Dynamic simulation is NOT required to obtain generator rotor speeds;
The number of PMUs typically allows us to calculate generator terminal bus voltage and current phasors;
- It is prioritized to place limited PMUs on generator
point of interconnection for monitoring and model
validation applications
No requirement of new communication link and the existing PDC can easily achieve that goal;
Robust estimator addresses PMU data quality issues.
[R5] J. B. Zhao, L. Mili, F. Milano, "Robust frequency divider for power system online monitoring and controls," IEEE Trans. Power Systems, vol. 33, no. 4, pp. 4414-4423, 2018.

## Slide 15: Robust Bus Frequency Estimator
The electromechanical dynamics can be captured by the swing equations as follows:
[R5] J. B. Zhao, L. Mili, F. Milano, "Robust frequency divider for power system online monitoring and controls," IEEE Trans. Power Systems, vol. 33, no. 4, pp. 4414-4423, 2018.
where is the rotor angle; is the generator inertia constant; and are the generator mechanical power and electrical power outputs, respectively.
Remark: can be calculated from PMU measurements while is a constant or has small variations during transient process.

## Slide 16: Robust Bus Frequency Estimator
If and are taken as swing equations inputs and the derived internal generator frequency is the output, a state-space model can be obtained.
[R5] J. B. Zhao, L. Mili, F. Milano, "Robust frequency divider for power system online monitoring and controls," IEEE Trans. Power Systems, vol. 33, no. 4, pp. 4414-4423, 2018.
where
, is a constant matrix,

## Slide 17: Derive Generator Internal Frequency
Rotor speed is the rate of change of rotor angle while bus frequency is the rate of change of the phase of the voltage measured at the bus. Thus, the internal rotor speed is NOT equal to the bus frequency;
[R5] J. B. Zhao, L. Mili, F. Milano, "Robust frequency divider for power system online monitoring and controls," IEEE Trans. Power Systems, vol. 33, no. 4, pp. 4414-4423, 2018.
where vector is the internal generator voltage phasor.
Remark: Using the Kay FIR filter, internal rotor angle frequency can be derived and measurement vector is obtained.
However, there still exists relationship between the internal rotor angle and bus voltage phasor as follows:

## Slide 18: Generator Rotor Speed Estimation
Since it is a linear state-space model, Kalman filter can be directly used to estimate rotor speed and angle:
[R5] J. B. Zhao, L. Mili, F. Milano, "Robust frequency divider for power system online monitoring and controls," IEEE Trans. Power Systems, vol. 33, no. 4, pp. 4414-4423, 2018.
Prediction:
Filtering:
where is the Kalman gain and is state estimation covariance matrix.

## Slide 19
Outlier detection using PS
We propose to apply PS on the following matrix
Time instants:
has two columns to measure temporal correlations. It is found two continuous samples are sufficient to detect outliers effectively.
PS is applied to the innovation vectors and the predicted state vector separately.
Innovation vectors

## Slide 20: Detecting Outliers by PS
Projection statistics is defined and calculated by

## Slide 21: Robust Filtering
arg
New weighting function:
Robust filtering via the GM-estimator that minimizes an objective function given by

## Slide 22: Bus and COI Frequency Estimation
When the rotor speed and rotor angle of each generator are obtained, they are communicated to the control center for bus frequency estimation using the following equation:
An interesting natural byproduct of the proposed bus frequency estimator is the calculation of real-time center of inertia (COI) frequency:
Remark: can be augmented with state vector for joint estimation in case it is unknown.

## Slide 23: Results on IEEE 39-bus system
Disturbance: at t=0.5 seconds, the Generator 4 connected to bus 33 is tripped.
Generator model: two-axis model with IEEE DC1A excitation system and TGOV1 turbine-governor.

## Slide 24
Case 1: Non-Gaussian Noise
Case 1: Noisy PMU Measurements
Comparing the estimated frequency at bus 34 by DUKF, RDUKF and D-method with normal measurement noise in the IEEE 39-bus system.
DUKF: proposed non-robust KF based method
RDUKF: proposed robust KF based method
D-method: frequency divider

## Slide 25
Case 1: Non-Gaussian Noise
Case 2: Bad PMU Measurements
The derived rotor speed of Generator 5 by PMU measurements is contaminated with 20% error from t = 4 s to t = 6 s

## Slide 26
Case 1: Non-Gaussian Noise
Case 3: COI Frequency Monitoring
[R6] J. B. Zhao, Y. Tang, V. Terzija, "Robust Online Estimation of Power System Center of Inertia Frequency," IEEE Trans. Power Systems, vol. 34, no. 1, pp. 821-825, 2019.
Estimate COI when the parameter values of the transmission system lines and transformer are with 1%–5% uncertainties.

## Slide 27
Case 1: Non-Gaussian Noise
Case 4: Missing PMU Measurements
Estimate frequency at bus 73 with missing PMU measurement in the IEEE 145-bus system. The generator located at bus 106 is tripped at t = 0.5s.

## Slide 28: Conclusions
Accurate bus frequency information plays an important role for system monitoring & control;
The proposed method is able to estimate all bus frequencies with limited number of PMUs;
The hierarchical and decentralized framework allows us to estimate large-scale system bus frequencies in an online manner;
Field validation of the developed method as well as consideration of communication delays will be our future work.

## Slide 29: References
29
J. B. Zhao, Y. Tang, V. Terzija, "Robust online estimation of power system center of inertia frequency," IEEE Trans. Power Systems, vol. 34, no. 1, pp. 821-825, 2019.
J. B. Zhao, L. Mili, F. Milano, "Robust frequency divider for power system online monitoring and controls," IEEE Trans. Power Systems, vol. 33, no. 4, pp. 4414-4423, 2018.
J. B. Zhao, L. Mili, "A robust generalized-maximum likelihood unscented Kalman filter for power system dynamic state estimation," IEEE Journal of Selected Topics in Signal Processing, vol. 12, no. 4, pp. 578-592, 2018.
F. Milano and A. Ortega, “Frequency divider,” IEEE Trans. Power Syst., vol. 32, no. 2, pp. 1493–1501, Mar. 2017.